## Cover
Net Zero Building Retrofit Guides
Fuel Switching Options

## Fuel Switching Options
Fuel Switching Options
Fuel switching is the most important step for reducing operational emissions, and involves replacing natural gas or fossil fuel-based systems with electric alternatives. This tool can be used to identify technology options to switch your building systems to electric sources.
Fuel Switch the with one of the following technology options:
Instructions - To begin, input the characteristics of your building. Then select a building system to analyze. Lastly, if known, input the building's current energy data.
The following technology option(s) can be implemented in your building or home to enable you to fuel switch from fossil fuels, such as natural gas. Review and compare the provided option(s) to determine which works best for your building. If only one option is provided, assess whether it is suitable for your building.
[5 empty] | Equipment # 1 | No match | Equipment # 2 | No match | Equipment # 3 | No match
❶ Input your building characteristics
Building Type:
Building Type Assumption:
| Area: |  | ft²
❷ Select building system to analyze
System Type:
*Ensure the building type is entered before selecting the system type.
[5 empty] | Energy Use Reduction |  | Energy Use Reduction |  | Energy Use Reduction
❸ Input your building energy data
Enter your building energy use (if known). If your energy use is not known, the following default values will be used based on the building characteristics you inputted:
[5 empty] | Utility Cost Reduction |  | Utility Cost Reduction |  | Utility Cost Reduction
Default energy use:
[5 empty] | GHG Emissions Reductions |  | GHG Emissions Reductions |  | GHG Emissions Reductions
| Natural Gas Use: |  | m3/year | 0 m³/year
| Electricity Use: |  | kWh/year | 0 kWh/year
[5 empty] | Considerations |  | Considerations |  | Considerations
Connected to district heating system?
| District Heating Rate: |  | ekWh/year | 0 ekWh/year
Enter energy use cost rates (if known)
If energy rates are not known, the following default values will be used:
Default rate:
[5 empty] | Technology Companion Guide |  | Technology Companion Guide |  | Technology Companion Guide
| Natural Gas Rate: |  | /m3 | $0.15 / m³
| Electricity Rate: |  | /kWh | $0.13 / kWh
| District Heating Rate: |  | /ekWh | $0.11 / ekWh ⓘ
Note on G60: Note District energy costs vary widely, so it is strongly recommended to enter a user-defined district heating rate. Review your district energy utility bill or contact your provider to obtain this rate.

## Tool Calc Sheet (hidden)
Tool Calc Sheet
Metric | Unit |  | Notes
Retrofit Measure | Text | 0 | Pull from front end
Building Type | Text | 0 | Pull from front end
Vintage | Text | #N/A | Pull from Existing Building EUI Database
Area | ft2 | 0 | Pull from front end
Area | m2 | 0 | Formula - Converts to m2
Natural Gas Use Intensity | kWh/m2 | 0 | Pull from Existing Building EUI Database
Electricity Use Intensity | kWh/m2 | 0 | Pull from Existing Building EUI Database
Total Energy Use Intensity | kWh/m2 | 0 | Pull from Existing Building EUI Database
Existing Building Values
Existing NG Use Default | kWh | 0 | Formula - area * energy use intensity
Existing NG Use Default | m3 | 0 | Formula - Converts to m3
Existing NG Use User Input | m3 | 0 | Pull from front end
Existing NG Use User Input | kWh | 0 | Formula - Converts to m3
Natural Gas Use | kWh | 0 | Formula - NG Use Default or User Input
Existing Electricity Use Default | kWh | 0 | Formula - area * energy use intensity
Existing Electricity Use User Input | kWh | 0 | Pull from front end
Electricity Use | kWh | 0 | Formula - Elec Use Default or User Input
Connect to DES? | Y/N | 0 | Pull from front end
Existing Districy Use Default | kWh | 0 | Formula - area * energy use intensity
Existing District Use User Input | kWh | 0 | Pull from front end
District Use | kWh | 0 | Formula - DES Use Default or User Input
Existing Total Energy Use | kWh | 0 | Formula elec use kWh + NG use kWh
NG Emission Rate | kg CO2e/m3 | 1.921 | Constant Value
NG Emission Rate | kg CO2e/kWh | 0.18209 | Formula - Converts to kWh
Electricity Emission Rate | kg CO2e/kWh | 0.038 | Constant Value | Rounding Table
District Emission Rate | kg CO2e/kWh | 0.21719 | Constant Value - District Steam Rate | 0 | 0
Low Carbon District Emission Rate | kg CO2e/kWh | 0.05 | Constant Value - Assumed Low Carbon District Energy Rate (BC DES Calculator Tier 2) https://www2.gov.bc.ca/assets/gov/environment/climate-change/cng/calculators/des_calculator.xlsx | 10 | 0
Existing NG Emissions (kg CO2e) | kg CO2e | 0 | Formula - energy Use * Emission Rate | 100 | -1
Existing Electricity Emissions (kg CO2e) | kg CO2e | 0 | Formula - energy Use * Emission Rate | 199 | -1
Existing District Energy Emissions (kg CO2e) | kg CO2e | 0 | Formula - energy Use * Emission Rate | 1000 | -2
Existing Total Emissions (kg CO2e) | kg CO2e | 0 | Formula - Sum of emissions | 10000 | -3
|  |  |  | 1000000 | -4
Existing NG Rate Default | $/m3 | 0.15 | Constant Value
Existing NG Rate Default | $/kWh | 0.014218 | Formula - Converts to kWh
Existing NG Rate User Input | $/m3 | 0 | Pull from front end
Existing NG Rate User Input | $/kWh | 0 | Formula - Converts to kWh
NG Rate for Project | $/kWh | 0.014218 | Formula - NG Use Default or User Input
Existing Electricity Rate Default | $/kWh | 0.13033 | Constant Value
Existing Electricity Rate User Input | $/kWh | 0 | Pull from front end
Electricity Rate for Project | $/kWh | 0.13033 | Formula - Elec Use Default or User Input
Existing District Energy Rate Default | $/kWh | 0.11 | Constant Value
Existing District Energy Rate User Input | $/kWh | 0 | Pull from front end
District Energy Rate for Project | $/kWh | 0.11 | Formula - DES Use Default or User Input
Existing Electricity Cost | $ | 0 | Formula - energy use * energy cost
Exsiting Natural Gas Cost | $ | 0 | Formula - energy use * energy cost
Exsiting District Energy Cost | $ | 0 | Formula - energy use * energy cost
Existing Total Energy Costs | $ | 0 | Formula - energy use * energy cost
Energy Savings
|  | Option 1 |  |  | Absolute | % Savings
Type of retrofit option | text | No match |  | Energy Savings | #N/A | #N/A
Natural Gas Use - LOW | kwh | #N/A |  | Energy Cost Reduction | #N/A | #N/A
Natural Gas Use - HIGH | kwh | #N/A |  | Annual Emission Reduction | #N/A | #N/A
Electricity Use - LOW | kwh | #N/A |  | Considerations | #N/A
Electricity Use - HIGH | kwh | #N/A |  | Technology Companion Guide | #N/A
District Energy Use - LOW | kwh | #N/A
District Energy Use - HIGH | kwh | #N/A
Total Energy Use Savings - LOW | kwh | #N/A
Total Energy Use Savings- HIGH | kwh | #N/A
Total Energy Savings (%) - LOW | % | #N/A
Total Energy Savings (%) - HIGH | % | #N/A
Operational Costs - LOW | $ | #N/A
Operational Costs - HIGH | $ | #N/A
Operational Costs Savings - LOW | % | #N/A
Operational Costs Savings - HIGH | % | #N/A
GHG Emissions Savings - LOW | kg CO2e | #N/A
GHG Emissions Savings - HIGH | kg CO2e | #N/A
GHG Emissions - LOW | % | #N/A
GHG Emissions - HIGH | % | #N/A
Image |  | Empty | 0
|  | Option 2 |  |  | Absolute | % Savings
Type of retrofit option | text | No match |  | Energy Savings | #N/A | #N/A
Natural Gas Use - LOW | kwh | #N/A |  | Energy Cost Reduction | #N/A | #N/A
Natural Gas Use - HIGH | kwh | #N/A |  | Annual Emission Reduction | #N/A | #N/A
Electricity Use - LOW | kwh | #N/A |  | Considerations | #N/A
Electricity Use - HIGH | kwh | #N/A |  | Technology Companion Guide | #N/A
District Energy Use - LOW | kwh | #N/A
District Energy Use - HIGH | kwh | #N/A
Total Energy Use Savings - LOW | kwh | #N/A
Total Energy Use Savings- HIGH | kwh | #N/A
Total Energy Savings (%) - LOW | % | #N/A
Total Energy Savings (%) - HIGH | % | #N/A
Operational Costs - LOW | $ | #N/A
Operational Costs - HIGH | $ | #N/A
Operational Costs Savings - LOW | % | #N/A
Operational Costs Savings - HIGH | % | #N/A
GHG Emissions - LOW | kg CO2e | #N/A
GHG Emissions - HIGH | kg CO2e | #N/A
GHG Emissions - LOW | % | #N/A
GHG Emissions - HIGH | % | #N/A
Image |  | Empty
|  | Option 3 |  |  | Absolute | % Savings
Type of retrofit option |  | No match |  | Energy Savings | #N/A | #N/A
Natural Gas Use - LOW |  | #N/A |  | Energy Cost Reduction | #N/A | #N/A
Natural Gas Use - HIGH |  | #N/A |  | Annual Emission Reduction | #N/A | #N/A
Electricity Use - LOW |  | #N/A |  | Considerations | #N/A
Electricity Use - HIGH |  | #N/A |  | Technology Companion Guide | #N/A
District Energy Use - LOW |  | #N/A
District Energy Use - HIGH |  | #N/A
Total Energy Use Savings - LOW |  | #N/A
Total Energy Use Savings- HIGH |  | #N/A
Total Energy Savings (%) - LOW | % | #N/A
Total Energy Savings (%) - HIGH | % | #N/A
Operational Costs - LOW |  | #N/A
Operational Costs - HIGH |  | #N/A
Operational Costs Savings - LOW | % | #N/A
Operational Costs Savings - HIGH | % | #N/A
GHG Emissions - LOW |  | #N/A
GHG Emissions - HIGH |  | #N/A
GHG Emissions - LOW | % | #N/A
GHG Emissions - HIGH | % | #N/A
Image |  | Empty
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same comments, shouldn’t multiple by area. Should pull row 17 or 18 Reply: Agreed, formula is fixed
Note on D25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same comments, shouldn’t multiple by area. Should pull row 17 or 18 Reply: Agreed, formula is fixed

## Drop Down Database (hidden)
Building Type |  |  | Yes/No | Year | Hold Period | Retrofit List - Dynamic | Retrofit List - Dynamic | Building Types with Gas Appliances
Mid Rise Office | 2 | Large | Yes | 2025 | 5 | 0 | 0 | Educational Facility
Educational Facility | 2 | Large | No | 2026 | 10 |  | 0 | Mixed Use
Big Box Store | 2 | Large |  | 2027 | 15 |  | 0 | Condominium
Low Rise Office | 2 | Large |  | 2028 | 20 |  | 0 | Low Rise Rental Apartment
Strip Mall | 2 | Large |  | 2029 | 25 |  | 0 | Single Family Home Attached
Mixed Use | 2 | Large |  | 2030 | 30 |  | 0 | Single Family Home Detached
Condominium | 2 | Large |  | 2031 |  |  | 0
Low Rise Rental Apartment | 2 | Large |  | 2032 |  |  | 0
Single Family Home Attached | 1 | Small |  | 2033 |  |  | 0
Single Family Home Detached | 1 | Small |  | 2034 |  |  | 0
|  |  |  | 2035 |  |  | 0
|  |  |  | 2036 |  |  | 0
|  |  |  | 2037 |  |  | 0
|  |  |  | 2038 |  |  | 0
|  |  |  | 2039 |  |  | 0
|  |  |  | 2040 |  |  | 0
|  |  |  | 2041 |  |  | 0
|  |  |  | 2042 |  |  | 0
|  |  |  | 2043 |  |  | 0
|  |  |  | 2044 |  |  | 0
|  |  |  | 2045 |  |  | 0
|  |  |  | 2046 |  |  | 0
|  |  |  | 2047 |  |  | 0
|  |  |  | 2048 |  |  | 0
|  |  |  | 2049 |  |  | 0
|  |  |  | 2050 |  |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Heating System Database (hidden)
Helper | System Type | Retrofit | Name | Image - Small Buildings | Image - Large Buildings | Considerations - Small Buildings | Considerations - Large Buildings | Technology Companion Guide - Small Buildings | Technology Companion Guide - Large Buildings
Domestic Hot WaterElectric water heaters | Domestic Hot Water | Electric water heaters | DHW_Electric_ |  |  | - Easy to install - Compact units ideal for small spaces - May require increased electrical capacity | - Easy to install - Compact units ideal for small spaces - May require increased electrical capacity | "Domestic Hot Water Systems" | "Domestic Hot Water Systems"
Domestic Hot WaterHeat Pump Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | DHW_HeatPump_ |  |  | - High upfront cost, lower operational costs - Requires area for air circulation - Ideally located in warmer spaces | - High upfront cost, lower operational costs - Requires area for air circulation - Ideally located in warmer spaces | "Domestic Hot Water Systems" | "Domestic Hot Water Systems"
Gas AppliancesElectric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Gas_Appliances_ |  |  | - Induction ranges require compatible pots and pans - Heat Pump Dryers have higher efficiency over standard electric ones - May require increased electrical capacity | - Induction ranges require compatible pots and pans - Heat Pump Dryers have higher efficiency over standard electric ones - May require increased electrical capacity | "Smart Homes and Appliances" | "Smart Homes and Appliances"
Gas AppliancesElectric and Induction Ranges | Gas Appliances | Electric and Induction Ranges | Gas_Ranges_ |  |  | - Require compatible pots and pans - Reduced burn risk - Higher efficiency over standard electric ranges - May require increased electrical demand capacity | - Require compatible pots and pans - Reduced burn risk - Higher efficiency over standard electric ranges - May require increased electrical demand capacity | "Smart Homes and Appliances" | "Smart Homes and Appliances"
Heating SystemAir source heat pumps | Heating System | Air source heat pumps | Heating_ASHP_ |  |  | - More effective when paired with envelope efficiency retrofits - May require backup system in cold temperatures - May require increased electrical demand capacity | - Requires rooftop area - More effective when paired with envelope efficiency retrofits - May require backup system in cold temperatures - May require increased electrical demand capacity | "Air Source Heat Pumps For Homes and Small Buildings" | "Air Source Heat Pumps For Large Buildings"
Heating SystemLow Carbon District Energy System | Heating System | Low Carbon District Energy System | Heating_District_ |  |  | - Requires proximity to district energy system | - Requires proximity to district energy system | "Low Carbon District Energy" | "Low Carbon District Energy"
Heating SystemGround Source Heat Pumps | Heating System | Ground Source Heat Pumps | Heating_GSHP_ |  |  | - Requires land for boreholes - Effective during cold temperatures - High upfront cost, lower operational costs | - Requires land for boreholes - Effective during cold temperatures - High upfront cost, lower operational costs | "Ground Source Heat Pumps" | "Ground Source Heat Pumps"
Empty |  |  | Empty

## Existing Building EUI (hidden)
Existing Building EUI Database
Source: City of Toronto Net Zero Existing Buildings Strategy - Impact Modeling & Assessment Technical Appendix May 2021
Building Type | Cluster | Fuel Energy (kWh/m²) | Electric Energy (kWh/m²) | TEUI (kWh/ m²) | Building Vintage (Selected in Phase 2)
Unit: | 0 | 0 | 0 | 0
Mid Rise Office | 14 | 270 | 219 | 489 | 20-storey structure, 1975 construction
Educational Facility | 4 | 201 | 284 | 485 | 2-storey structure, 1965 construction
Big Box Store | 13 | 159 | 231 | 389 | 1-storey structure, 1980 construction, >100,000 ft²
Low Rise Office | 10 | 149 | 204 | 353 | 2-storey structure, 1970 construction
Strip Mall | 7 | 127 | 248 | 375 | 1-storey structure, 1950 construction, <100,000 ft²
Single Family Home Attached | 30 | 147 | 43 | 190 | 3-storey structure, 1990 construction
Single Family Home Detached | 23 | 203 | 38 | 241 | 2-storey structure, 1910 construction
Low Rise Rental Apartment | 8 | 234 | 107 | 341 | 4-storey structure, 1960 construction
Condominium | 12 | 215 | 93 | 308 | 13-storey structure, 2000 construction
Mixed Use | 22 | 268 | 322 | 590 | 20-storey structure, 1980 construction

## Retrofit Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111
Helper Column | Helper Column | Helper Column | Retrofit Measure | System Type | Retrofit | Building Type | Total EUI - Lower | Total - EUI - Upper | GHGI Lower | GHGI Upper | GHGI Average | Natural Gas (kwh/m2) | Electricity (kwh/m2) | % NG - LOW | % NG - HIGH | %Elec - LOW | %Elec - HIGH | % DES Added - LOW | % DES Added - HIGH | % Elec Added - LOW | % Elec Added - HIGH | Natural Gas - EUI LOW | Natural Gas - EUI HIGH | Electricity - EUI LOW | Electricity - EUI HIGH | DES - EUI LOW | DES - EUI HIGH | Total EUI Reduction - LOW | Total EUI Reduction - HIGH
Domestic Hot WaterMid Rise Office-1 | Domestic Hot WaterMid Rise Office | Heat Pump Water HeatersMid Rise Office | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Mid Rise Office | 1% | 4% | 1% | 10% | 5.5% | 270 | 219 | 2% | 10% | 0% | 0% | 0% | 0% | -0.5% | -2.5% | 264.6 | 243 | 220.35 | 225.75 | 0 | 0 | 0.8282% | 4.141%
Heating SystemMid Rise Office-1 | Heating SystemMid Rise Office | Low Carbon District Energy SystemMid Rise Office | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 85% | 95% | 5% | 10% | -59.5% | -66.5% | 0% | 0% | 40.5 | 13.5 | 208.05 | 197.1 | 160.65 | 179.55 | 16.32% | 20.21%
Heating SystemMid Rise Office-2 | Heating SystemMid Rise Office | Air Source Heat PumpsMid Rise Office | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 85% | 95% | 5% | 10% | 0% | 0% | -42.5% | -47.5% | 40.5 | 13.5 | 322.8 | 325.35 | 0 | 0 | 25.71% | 30.71%
Heating SystemMid Rise Office-3 | Heating SystemMid Rise Office | Ground Source Heat PumpsMid Rise Office | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 85% | 95% | 5% | 10% | 0% | 0% | -28.33% | -31.67% | 40.5 | 13.5 | 284.55 | 282.6 | 0 | 0 | 33.53% | 39.45%
Domestic Hot WaterEducational Facility-1 | Domestic Hot WaterEducational Facility | Heat Pump Water HeatersEducational Facility | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Educational Facility | 1% | 5% | 1% | 15% | 8% | 201 | 284 | 2% | 15% | 0% | 0% | 0% | 0% | -0.5% | -3.75% | 196.98 | 170.85 | 285.005 | 291.5375 | 0 | 0 | 0.6216% | 4.662%
Heating SystemEducational Facility-1 | Heating SystemEducational Facility | Low Carbon District Energy SystemEducational Facility | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 80% | 98% | 5% | 8% | -56% | -68.6% | 0% | 0% | 40.2 | 4.02 | 269.8 | 261.28 | 112.56 | 137.886 | 12.87% | 16.87%
Heating SystemEducational Facility-2 | Heating SystemEducational Facility | Air Source Heat PumpsEducational Facility | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 80% | 98% | 5% | 8% | 0% | 0% | -40% | -49% | 40.2 | 4.02 | 350.2 | 359.77 | 0 | 0 | 19.51% | 24.99%
Heating SystemEducational Facility-3 | Heating SystemEducational Facility | Ground Source Heat PumpsEducational Facility | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 80% | 98% | 5% | 8% | 0% | 0% | -26.67% | -32.67% | 40.2 | 4.02 | 323.4 | 326.94 | 0 | 0 | 25.03% | 31.76%
Gas AppliancesEducational Facility-1 | Gas AppliancesEducational Facility | Electric and Induction RangesEducational Facility | Gas Appliances - Electric and Induction Ranges | Gas Appliances | Electric and Induction Ranges | Educational Facility | 1% | 10% | 10% | 15% | 12.5% | 201 | 284 | 5% | 15% | 0% | 0% | 0% | 0% | -2.5% | -7.5% | 190.95 | 170.85 | 289.025 | 299.075 | 0 | 0 | 1.036% | 3.108%
Domestic Hot WaterBig Box Store-1 | Domestic Hot WaterBig Box Store | Electric Water HeatersBig Box Store | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Big Box Store | 1% | 5% | 1% | 10% | 5.5% | 159 | 231 | 2% | 15% | 0% | 0% | 0% | 0% | -0.5% | -3.75% | 155.82 | 135.15 | 231.795 | 236.9625 | 0 | 0 | 0.6115% | 4.587%
Heating SystemBig Box Store-1 | Heating SystemBig Box Store | Air Source Heat PumpsBig Box Store | Heating & Cooling System - Rooftop Air Source Heat Pumps with Backup Electric Heat | Heating System | Air Source Heat Pumps | Big Box Store | 11% | 20% | 30% | 55% | 42.5% | 159 | 231 | 85% | 90% | 5% | 8% | 0% | 0% | -42.5% | -45% | 23.85 | 15.9 | 287.025 | 284.07 | 0 | 0 | 20.29% | 23.08%
Domestic Hot WaterLow Rise Office-1 | Domestic Hot WaterLow Rise Office | Heat Pump Water HeatersLow Rise Office | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Low Rise Office | 1% | 5% | 1% | 10% | 5.5% | 149 | 204 | 2% | 15% | 0% | 0% | 0% | 0% | -0.5% | -3.75% | 146.02 | 126.65 | 204.745 | 209.5875 | 0 | 0 | 0.6331% | 4.749%
Heating SystemLow Rise Office-1 | Heating SystemLow Rise Office | Air Source Heat PumpsLow Rise Office | Heating, Cooling, Ventilation Systems - Rooftop Air Source Heat Pump with Electric Baseboard | Heating System | Air Source Heat Pumps | Low Rise Office | 21% | 30% | 30% | 75% | 52.5% | 149 | 204 | 85% | 97% | 8% | 10% | 0% | 0% | -42.5% | -48.5% | 22.35 | 4.47 | 251.005 | 255.865 | 0 | 0 | 22.56% | 26.25%
Domestic Hot WaterStrip Mall-1 | Domestic Hot WaterStrip Mall | Electric Water HeatersStrip Mall | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Strip Mall | 1% | 5% | 1% | 10% | 5.5% | 127 | 248 | 2% | 20% | 0% | 0% | 0% | 0% | -0.5% | -5% | 124.46 | 101.6 | 248.635 | 254.35 | 0 | 0 | 0.508% | 5.08%
Heating SystemStrip Mall-1 | Heating SystemStrip Mall | Air Source Heat PumpsStrip Mall | Heating & Cooling System - Rooftop Air Source Heat Pumps with Backup Electric Heat | Heating System | Air Source Heat Pumps | Strip Mall | 12% | 25% | 20% | 55% | 37.5% | 127 | 248 | 80% | 97% | 8% | 10% | 0% | 0% | -40% | -48.5% | 25.4 | 3.81 | 278.96 | 284.795 | 0 | 0 | 18.84% | 23.04%
Domestic Hot WaterMixed Use-1 | Domestic Hot WaterMixed Use | Heat Pump Water HeatersMixed Use | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Mixed Use | 11% | 20% | 21% | 30% | 25.5% | 268 | 322 | 20% | 40% | 0% | 0% | 0% | 0% | -5% | -10% | 214.4 | 160.8 | 335.4 | 348.8 | 0 | 0 | 6.814% | 13.63%
Heating SystemMixed Use-1 | Heating SystemMixed Use | Low Carbon District Energy SystemMixed Use | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 70% | 80% | 8% | 10% | -49% | -56% | 0% | 0% | 80.4 | 53.6 | 296.24 | 289.8 | 131.32 | 150.08 | 13.91% | 16.36%
Heating SystemMixed Use-2 | Heating SystemMixed Use | Air Source Heat PumpsMixed Use | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 70% | 80% | 8% | 10% | 0% | 0% | -35% | -40% | 80.4 | 53.6 | 390.04 | 397 | 0 | 0 | 20.26% | 23.63%
Heating SystemMixed Use-3 | Heating SystemMixed Use | Ground Source Heat PumpsMixed Use | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 70% | 80% | 8% | 10% | 0% | 0% | -23.33% | -26.67% | 80.4 | 53.6 | 358.7733 | 361.2667 | 0 | 0 | 25.56% | 29.68%
Gas AppliancesMixed Use-1 | Gas AppliancesMixed Use | Electric and Induction Ranges & Heat Pump Electric DryersMixed Use | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Mixed Use | 1% | 10% | 5% | 25% | 15% | 268 | 322 | 1% | 15% | 0% | 0% | 0% | 0% | -0.5% | -7.5% | 265.32 | 227.8 | 323.34 | 342.1 | 0 | 0 | 0.2271% | 3.407%
Domestic Hot WaterCondominium-1 | Domestic Hot WaterCondominium | Heat Pump Water HeatersCondominium | Domestic Hot Water - Heat pump and electric resistance water heaters | Domestic Hot Water | Heat Pump Water Heaters | Condominium | 1% | 10% | 1% | 10% | 5.5% | 215 | 93 | 1% | 20% | 0% | 0% | 0% | 0% | -0.25% | -5% | 212.85 | 172 | 93.5375 | 103.75 | 0 | 0 | 0.5235% | 10.47%
Heating SystemCondominium-1 | Heating SystemCondominium | Low Carbon District Energy SystemCondominium | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 50% | 60% | 3% | 5% | -35% | -42% | 0% | 0% | 107.5 | 86 | 90.21 | 88.35 | 75.25 | 90.3 | 11.38% | 14.07%
Heating SystemCondominium-2 | Heating SystemCondominium | Air Source Heat PumpsCondominium | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 50% | 60% | 3% | 5% | 0% | 0% | -25% | -30% | 107.5 | 86 | 143.96 | 152.85 | 0 | 0 | 18.36% | 22.45%
Heating SystemCondominium-3 | Heating SystemCondominium | Ground Source Heat PumpsCondominium | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 50% | 60% | 3% | 5% | 0% | 0% | -16.67% | -20% | 107.5 | 86 | 126.0433 | 131.35 | 0 | 0 | 24.17% | 29.43%
Gas AppliancesCondominium-1 | Gas AppliancesCondominium | Electric and Induction Ranges & Heat Pump Electric DryersCondominium | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Condominium | 1% | 10% | 5% | 20% | 12.5% | 215 | 93 | 2% | 15% | 0% | 0% | 0% | 0% | -1% | -7.5% | 210.7 | 182.75 | 95.15 | 109.125 | 0 | 0 | 0.6981% | 5.235%
Domestic Hot WaterLow Rise Rental Apartment-1 | Domestic Hot WaterLow Rise Rental Apartment | Heat Pump Water HeatersLow Rise Rental Apartment | Domestic Hot Water - Heat pump and electric resistance water heaters | Domestic Hot Water | Heat Pump Water Heaters | Low Rise Rental Apartment | 11% | 20% | 21% | 30% | 25.5% | 234 | 107 | 22% | 30% | 0% | 0% | 0% | 0% | -5.5% | -7.5% | 182.52 | 163.8 | 119.87 | 124.55 | 0 | 0 | 11.32% | 15.44%
Heating SystemLow Rise Rental Apartment-1 | Heating SystemLow Rise Rental Apartment | Low Carbon District Energy SystemLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - District Energy System + Energy Recovery Ventilators | Heating System | Low Carbon District Energy System | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 70% | 80% | 8% | 10% | -49% | -56% | 0% | 0% | 70.2 | 46.8 | 98.44 | 96.3 | 114.66 | 131.04 | 16.92% | 19.61%
Heating SystemLow Rise Rental Apartment-2 | Heating SystemLow Rise Rental Apartment | Air Source Heat PumpsLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - Air Source Heat Pumps + Energy Recovery Ventilators | Heating System | Air Source Heat Pumps | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 70% | 80% | 8% | 10% | 0% | 0% | -35% | -40% | 70.2 | 46.8 | 180.34 | 189.9 | 0 | 0 | 26.53% | 30.59%
Heating SystemLow Rise Rental Apartment-3 | Heating SystemLow Rise Rental Apartment | Ground Source Heat PumpsLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - Ground Source Heat Pumps + Energy Recovery Ventilators | Heating System | Ground Source Heat Pumps | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 70% | 80% | 8% | 10% | 0% | 0% | -23.33% | -26.67% | 70.2 | 46.8 | 153.04 | 158.7 | 0 | 0 | 34.53% | 39.74%
Gas AppliancesLow Rise Rental Apartment-1 | Gas AppliancesLow Rise Rental Apartment | Electric and Induction Ranges & Heat Pump Electric DryersLow Rise Rental Apartment | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Low Rise Rental Apartment | 1% | 10% | 5% | 20% | 12.5% | 234 | 107 | 2% | 15% | 0% | 0% | 0% | 0% | -1% | -7.5% | 229.32 | 198.9 | 109.34 | 124.55 | 0 | 0 | 0.6862% | 5.147%
Domestic Hot WaterSingle Family Home Attached-1 | Domestic Hot WaterSingle Family Home Attached | Electric Water HeatersSingle Family Home Attached | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Single Family Home Attached | 11% | 20% | 11% | 20% | 15.5% | 147 | 43 | 20% | 30% | 0% | 0% | 0% | 0% | -5% | -7.5% | 117.6 | 102.9 | 50.35 | 54.025 | 0 | 0 | 11.61% | 17.41%
Heating SystemSingle Family Home Attached-1 | Heating SystemSingle Family Home Attached | Air Source Heat PumpsSingle Family Home Attached | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Single Family Home Attached | 1% | 45% | 1% | 45% | 23% | 147 | 43 | 60% | 80% | 1% | 5% | 0% | 0% | -30% | -40% | 58.8 | 29.4 | 86.67 | 99.65 | 0 | 0 | 23.44% | 32.08%
Heating SystemSingle Family Home Attached-2 | Heating SystemSingle Family Home Attached | Ground Source Heat PumpsSingle Family Home Attached | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Single Family Home Attached | 1% | 45% | 1% | 45% | 23% | 147 | 43 | 60% | 80% | 1% | 5% | 0% | 0% | -20% | -26.67% | 58.8 | 29.4 | 71.97 | 80.05 | 0 | 0 | 31.17% | 42.39%
Gas AppliancesSingle Family Home Attached-1 | Gas AppliancesSingle Family Home Attached | Electric and Induction Ranges & Heat Pump Electric DryersSingle Family Home Attached | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Single Family Home Attached | 1% | 10% | 5% | 20% | 12.5% | 147 | 43 | 2% | 15% | 0% | 0% | 0% | 0% | -1% | -7.5% | 144.06 | 124.95 | 44.47 | 54.025 | 0 | 0 | 0.7737% | 5.803%
Domestic Hot WaterSingle Family Home Detached-1 | Domestic Hot WaterSingle Family Home Detached | Electric Water HeatersSingle Family Home Detached | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Single Family Home Detached | 21% | 30% | 21% | 30% | 25.5% | 203 | 38 | 20% | 30% | 0% | 0% | 0% | 0% | -5% | -7.5% | 162.4 | 142.1 | 48.15 | 53.225 | 0 | 0 | 12.63% | 18.95%
Heating SystemSingle Family Home Detached-1 | Heating SystemSingle Family Home Detached | Air Source Heat PumpsSingle Family Home Detached | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Single Family Home Detached | 1% | 55% | 1% | 55% | 28% | 203 | 38 | 60% | 80% | 1% | 5% | 0% | 0% | -30% | -40% | 81.2 | 40.6 | 98.52 | 117.3 | 0 | 0 | 25.43% | 34.48%
Heating SystemSingle Family Home Detached-2 | Heating SystemSingle Family Home Detached | Ground Source Heat PumpsSingle Family Home Detached | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Single Family Home Detached | 1% | 55% | 1% | 55% | 28% | 203 | 38 | 60% | 80% | 1% | 5% | 0% | 0% | -20% | -26.67% | 81.2 | 40.6 | 78.22 | 90.2333 | 0 | 0 | 33.85% | 45.71%
Gas AppliancesSingle Family Home Detached-1 | Gas AppliancesSingle Family Home Detached | Electric and Induction Ranges & Heat Pump Electric DryersSingle Family Home Detached | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Single Family Home Detached | 1% | 10% | 5% | 20% | 12.5% | 203 | 38 | 2% | 15% | 0% | 0% | 0% | 0% | -1% | -7.5% | 198.94 | 172.55 | 40.03 | 53.225 | 0 | 0 | 0.8423% | 6.317%

## Retrofit Data - DES (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111
Helper Column | Helper Column | Helper Column | Retrofit Measure | System Type | Retrofit | Building Type | Total EUI - Lower | Total - EUI - Upper | GHGI Lower | GHGI Upper | GHGI Average | Natural Gas (kwh/m2) | Electricity (kwh/m2) | % NG - LOW | % NG - HIGH | %Elec - LOW | %Elec - HIGH | % DES Added - LOW | % DES Added - HIGH | % Elec Added - LOW | % Elec Added - HIGH | Natural Gas - EUI LOW | Natural Gas - EUI HIGH | Electricity - EUI LOW | Electricity - EUI HIGH | DES - EUI LOW | DES - EUI HIGH | Total EUI Reduction - LOW | Total EUI Reduction - HIGH
Domestic Hot WaterMid Rise Office-1 | Domestic Hot WaterMid Rise Office | Heat Pump Water HeatersMid Rise Office | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Mid Rise Office | 1% | 4% | 1% | 10% | 5.5% | 270 | 219 | 0% | 0% | 0% | 0% | 2% | 10% | -0.5% | -2.5% | 270 | 270 | 220.35 | 225.75 | -5.4 | 27 | 0.8282% | -6.902%
Domestic Hot WaterEducational Facility-1 | Domestic Hot WaterEducational Facility | Heat Pump Water HeatersEducational Facility | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Educational Facility | 1% | 5% | 1% | 15% | 8% | 201 | 284 | 0% | 0% | 0% | 0% | 2% | 15% | -0.5% | -3.75% | 201 | 201 | 285.005 | 291.5375 | -4.02 | 30.15 | 0.6216% | -7.771%
Domestic Hot WaterBig Box Store-1 | Domestic Hot WaterBig Box Store | Electric Water HeatersBig Box Store | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Big Box Store | 1% | 5% | 1% | 10% | 5.5% | 159 | 231 | 0% | 0% | 0% | 0% | 2% | 15% | -2% | -15% | 159 | 159 | 234.18 | 254.85 | -3.18 | 23.85 | 0% | -12.23%
Domestic Hot WaterLow Rise Office-1 | Domestic Hot WaterLow Rise Office | Heat Pump Water HeatersLow Rise Office | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Low Rise Office | 1% | 5% | 1% | 10% | 5.5% | 149 | 204 | 0% | 0% | 0% | 0% | 2% | 15% | -0.5% | -3.75% | 149 | 149 | 204.745 | 209.5875 | -2.98 | 22.35 | 0.6331% | -7.914%
Domestic Hot WaterStrip Mall-1 | Domestic Hot WaterStrip Mall | Electric Water HeatersStrip Mall | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Strip Mall | 1% | 5% | 1% | 10% | 5.5% | 127 | 248 | 0% | 0% | 0% | 0% | 2% | 20% | -2% | -20% | 127 | 127 | 250.54 | 273.4 | -2.54 | 25.4 | 1.516e-14% | -13.55%
Domestic Hot WaterMixed Use-1 | Domestic Hot WaterMixed Use | Heat Pump Water HeatersMixed Use | Domestic Hot Water - Heat Pump and Electric Resistance Water Heaters | Domestic Hot Water | Heat Pump Water Heaters | Mixed Use | 11% | 20% | 21% | 30% | 25.5% | 268 | 322 | 0% | 0% | 0% | 0% | 20% | 40% | -5% | -10% | 268 | 268 | 335.4 | 348.8 | -53.6 | 107.2 | 6.814% | -22.71%
Domestic Hot WaterCondominium-1 | Domestic Hot WaterCondominium | Heat Pump Water HeatersCondominium | Domestic Hot Water - Heat pump and electric resistance water heaters | Domestic Hot Water | Heat Pump Water Heaters | Condominium | 1% | 10% | 1% | 10% | 5.5% | 215 | 93 | 0% | 0% | 0% | 0% | 1% | 20% | -0.25% | -5% | 215 | 215 | 93.5375 | 103.75 | -2.15 | 43 | 0.5235% | -17.45%
Domestic Hot WaterLow Rise Rental Apartment-1 | Domestic Hot WaterLow Rise Rental Apartment | Heat Pump Water HeatersLow Rise Rental Apartment | Domestic Hot Water - Heat pump and electric resistance water heaters | Domestic Hot Water | Heat Pump Water Heaters | Low Rise Rental Apartment | 11% | 20% | 21% | 30% | 25.5% | 234 | 107 | 0% | 0% | 0% | 0% | 22% | 30% | -5.5% | -7.5% | 234 | 234 | 119.87 | 124.55 | -51.48 | 70.2 | 11.32% | -25.73%
Domestic Hot WaterSingle Family Home Attached-1 | Domestic Hot WaterSingle Family Home Attached | Electric Water HeatersSingle Family Home Attached | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Single Family Home Attached | 11% | 20% | 11% | 20% | 15.5% | 147 | 43 | 0% | 0% | 0% | 0% | 20% | 30% | -20% | -30% | 147 | 147 | 72.4 | 87.1 | -29.4 | 44.1 | 0% | -46.42%
Domestic Hot WaterSingle Family Home Detached-1 | Domestic Hot WaterSingle Family Home Detached | Electric Water HeatersSingle Family Home Detached | Domestic Hot Water - Electric Water Heater | Domestic Hot Water | Electric Water Heaters | Single Family Home Detached | 21% | 30% | 21% | 30% | 25.5% | 203 | 38 | 0% | 0% | 0% | 0% | 20% | 30% | -20% | -30% | 203 | 203 | 78.6 | 98.9 | -40.6 | 60.9 | -1.179e-14% | -50.54%
Gas AppliancesEducational Facility-1 | Gas AppliancesEducational Facility | Electric and Induction RangesEducational Facility | Gas Appliances - Electric and Induction Ranges | Gas Appliances | Electric and Induction Ranges | Educational Facility | 1% | 10% | 10% | 15% | 12.5% | 201 | 284 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 286.01 | 299.075 | 0 | 0 | 41.03% | 38.34%
Gas AppliancesMixed Use-1 | Gas AppliancesMixed Use | Electric and Induction Ranges & Heat Pump Electric DryersMixed Use | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Mixed Use | 1% | 10% | 5% | 25% | 15% | 268 | 322 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 324.68 | 342.1 | 0 | 0 | 44.97% | 42.02%
Gas AppliancesCondominium-1 | Gas AppliancesCondominium | Electric and Induction Ranges & Heat Pump Electric DryersCondominium | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Condominium | 1% | 10% | 5% | 20% | 12.5% | 215 | 93 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 95.15 | 109.125 | 0 | 0 | 69.11% | 64.57%
Gas AppliancesLow Rise Rental Apartment-1 | Gas AppliancesLow Rise Rental Apartment | Electric and Induction Ranges & Heat Pump Electric DryersLow Rise Rental Apartment | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Low Rise Rental Apartment | 1% | 10% | 5% | 20% | 12.5% | 234 | 107 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 109.34 | 124.55 | 0 | 0 | 67.94% | 63.48%
Gas AppliancesSingle Family Home Attached-1 | Gas AppliancesSingle Family Home Attached | Electric and Induction Ranges & Heat Pump Electric DryersSingle Family Home Attached | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Single Family Home Attached | 1% | 10% | 5% | 20% | 12.5% | 147 | 43 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 44.47 | 54.025 | 0 | 0 | 76.59% | 71.57%
Gas AppliancesSingle Family Home Detached-1 | Gas AppliancesSingle Family Home Detached | Electric and Induction Ranges & Heat Pump Electric DryersSingle Family Home Detached | Gas Appliances - Electric and Induction Ranges & Heat Pump Electric Dryers | Gas Appliances | Electric and Induction Ranges & Heat Pump Electric Dryers | Single Family Home Detached | 1% | 10% | 5% | 20% | 12.5% | 203 | 38 | 100% | 100% | 0% | 0% | 0% | 0% | -1% | -7.5% | 0 | 0 | 40.03 | 53.225 | 0 | 0 | 83.39% | 77.91%
Heating SystemMid Rise Office-1 | Heating SystemMid Rise Office | Low Carbon District Energy SystemMid Rise Office | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 270 | 270 | 219 | 219 | 0 | 0 | 0% | 0%
Heating SystemMid Rise Office-2 | Heating SystemMid Rise Office | Air Source Heat PumpsMid Rise Office | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 0% | 0% | 0% | 0% | 85% | 95% | -42.5% | -47.5% | 270 | 270 | 333.75 | 347.25 | -229.5 | 256.5 | 23.47% | -78.68%
Heating SystemMid Rise Office-3 | Heating SystemMid Rise Office | Ground Source Heat PumpsMid Rise Office | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Mid Rise Office | 20% | 30% | 30% | 75% | 52.5% | 270 | 219 | 0% | 0% | 0% | 0% | 85% | 95% | -28.33% | -31.67% | 270 | 270 | 295.5 | 304.5 | -229.5 | 256.5 | 31.29% | -69.94%
Heating SystemEducational Facility-1 | Heating SystemEducational Facility | Low Carbon District Energy SystemEducational Facility | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 201 | 201 | 284 | 284 | 0 | 0 | 0% | 0%
Heating SystemEducational Facility-2 | Heating SystemEducational Facility | Air Source Heat PumpsEducational Facility | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 0% | 0% | 0% | 0% | 80% | 98% | -40% | -49% | 201 | 201 | 364.4 | 382.49 | -160.8 | 196.98 | 16.58% | -60.92%
Heating SystemEducational Facility-3 | Heating SystemEducational Facility | Ground Source Heat PumpsEducational Facility | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Educational Facility | 21% | 30% | 30% | 75% | 52.5% | 201 | 284 | 0% | 0% | 0% | 0% | 80% | 98% | -26.67% | -32.67% | 201 | 201 | 337.6 | 349.66 | -160.8 | 196.98 | 22.1% | -54.15%
Heating SystemBig Box Store-1 | Heating SystemBig Box Store | Air Source Heat PumpsBig Box Store | Heating & Cooling System - Rooftop Air Source Heat Pumps with Backup Electric Heat | Heating System | Air Source Heat Pumps | Big Box Store | 11% | 20% | 30% | 55% | 42.5% | 159 | 231 | 0% | 0% | 0% | 0% | 85% | 90% | -42.5% | -45% | 159 | 159 | 298.575 | 302.55 | -135.15 | 143.1 | 17.33% | -55.04%
Heating SystemLow Rise Office-1 | Heating SystemLow Rise Office | Air Source Heat PumpsLow Rise Office | Heating, Cooling, Ventilation Systems - Rooftop Air Source Heat Pump with Electric Baseboard | Heating System | Air Source Heat Pumps | Low Rise Office | 21% | 30% | 30% | 75% | 52.5% | 149 | 204 | 0% | 0% | 0% | 0% | 85% | 97% | -42.5% | -48.5% | 149 | 149 | 267.325 | 276.265 | -126.65 | 144.53 | 17.94% | -61.42%
Heating SystemStrip Mall-1 | Heating SystemStrip Mall | Air Source Heat PumpsStrip Mall | Heating & Cooling System - Rooftop Air Source Heat Pumps with Backup Electric Heat | Heating System | Air Source Heat Pumps | Strip Mall | 12% | 25% | 20% | 55% | 37.5% | 127 | 248 | 0% | 0% | 0% | 0% | 80% | 97% | -40% | -48.5% | 127 | 127 | 298.8 | 309.595 | -101.6 | 123.19 | 13.55% | -49.28%
Heating SystemMixed Use-1 | Heating SystemMixed Use | Low Carbon District Energy SystemMixed Use | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 268 | 268 | 322 | 322 | 0 | 0 | 0% | 0%
Heating SystemMixed Use-2 | Heating SystemMixed Use | Air Source Heat PumpsMixed Use | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 0% | 0% | 0% | 0% | 70% | 80% | -35% | -40% | 268 | 268 | 415.8 | 429.2 | -187.6 | 214.4 | 15.9% | -54.51%
Heating SystemMixed Use-3 | Heating SystemMixed Use | Ground Source Heat PumpsMixed Use | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Mixed Use | 21% | 30% | 20% | 40% | 30% | 268 | 322 | 0% | 0% | 0% | 0% | 70% | 80% | -23.33% | -26.67% | 268 | 268 | 384.5333 | 393.4667 | -187.6 | 214.4 | 21.2% | -48.45%
Heating SystemCondominium-1 | Heating SystemCondominium | Low Carbon District Energy SystemCondominium | Heating & Cooling Systems - District Energy System | Heating System | Low Carbon District Energy System | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 215 | 215 | 93 | 93 | 0 | 0 | 0% | 0%
Heating SystemCondominium-2 | Heating SystemCondominium | Air Source Heat PumpsCondominium | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 0% | 0% | 0% | 0% | 50% | 60% | -25% | -30% | 215 | 215 | 146.75 | 157.5 | -107.5 | 129 | 17.45% | -62.82%
Heating SystemCondominium-3 | Heating SystemCondominium | Ground Source Heat PumpsCondominium | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Condominium | 11% | 20% | 21% | 30% | 25.5% | 215 | 93 | 0% | 0% | 0% | 0% | 50% | 60% | -16.67% | -20% | 215 | 215 | 128.8333 | 136 | -107.5 | 129 | 23.27% | -55.84%
Heating SystemLow Rise Rental Apartment-1 | Heating SystemLow Rise Rental Apartment | Low Carbon District Energy SystemLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - District Energy System + Energy Recovery Ventilators | Heating System | Low Carbon District Energy System | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 234 | 234 | 107 | 107 | 0 | 0 | 0% | 0%
Heating SystemLow Rise Rental Apartment-2 | Heating SystemLow Rise Rental Apartment | Air Source Heat PumpsLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - Air Source Heat Pumps + Energy Recovery Ventilators | Heating System | Air Source Heat Pumps | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 0% | 0% | 0% | 0% | 70% | 80% | -35% | -40% | 234 | 234 | 188.9 | 200.6 | -163.8 | 187.2 | 24.02% | -82.35%
Heating SystemLow Rise Rental Apartment-3 | Heating SystemLow Rise Rental Apartment | Ground Source Heat PumpsLow Rise Rental Apartment | Heating, Cooling, Ventilation Systems - Ground Source Heat Pumps + Energy Recovery Ventilators | Heating System | Ground Source Heat Pumps | Low Rise Rental Apartment | 21% | 30% | 31% | 40% | 35.5% | 234 | 107 | 0% | 0% | 0% | 0% | 70% | 80% | -23.33% | -26.67% | 234 | 234 | 161.6 | 169.4 | -163.8 | 187.2 | 32.02% | -73.2%
Heating SystemSingle Family Home Attached-1 | Heating SystemSingle Family Home Attached | Air Source Heat PumpsSingle Family Home Attached | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Single Family Home Attached | 1% | 45% | 1% | 45% | 23% | 147 | 43 | 0% | 0% | 0% | 0% | 60% | 80% | -30% | -40% | 147 | 147 | 87.1 | 101.8 | -88.2 | 117.6 | 23.21% | -92.84%
Heating SystemSingle Family Home Attached-2 | Heating SystemSingle Family Home Attached | Ground Source Heat PumpsSingle Family Home Attached | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Single Family Home Attached | 1% | 45% | 1% | 45% | 23% | 147 | 43 | 0% | 0% | 0% | 0% | 60% | 80% | -20% | -26.67% | 147 | 147 | 72.4 | 82.2 | -88.2 | 117.6 | 30.95% | -82.53%
Heating SystemSingle Family Home Detached-1 | Heating SystemSingle Family Home Detached | Air Source Heat PumpsSingle Family Home Detached | Heating & Cooling Systems - Air Source Heat Pumps | Heating System | Air Source Heat Pumps | Single Family Home Detached | 1% | 55% | 1% | 55% | 28% | 203 | 38 | 0% | 0% | 0% | 0% | 60% | 80% | -30% | -40% | 203 | 203 | 98.9 | 119.2 | -121.8 | 162.4 | 25.27% | -101.1%
Heating SystemSingle Family Home Detached-2 | Heating SystemSingle Family Home Detached | Ground Source Heat PumpsSingle Family Home Detached | Heating & Cooling Systems - Ground Source Heat Pumps | Heating System | Ground Source Heat Pumps | Single Family Home Detached | 1% | 55% | 1% | 55% | 28% | 203 | 38 | 0% | 0% | 0% | 0% | 60% | 80% | -20% | -26.67% | 203 | 203 | 78.6 | 92.1333 | -121.8 | 162.4 | 33.69% | -89.85%

## Retrofit Saving Database (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114
Key | Building Type | System Type | Baseline System | ASHRAE 90.1 | Retrofit Measure | ASHRAE 90.1 | Energy Use Reduction |  |  | UpFront Cost | Total EUI |  |  | NG Savings Upper Limit | NG Savings Upper Limit | Electricity Savings Upper Limit | Electricity Savings Upper Limit | GHGI Reduction | Total Energy Use Intensity | NG Use Intensity | Electricity Use Intensity
|  |  |  | COPs |  | COPs |  |  |  | $/ft2 | % |  |  | % | % | % | % | (CO2e/ft2) | kWh / m2 | kWh / m2 | kWh / m2
Mid Rise OfficeDomestic Hot WaterHeat pump and electric resistance water heaters | Mid Rise Office | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Heat pump and electric resistance water heaters | 3 | -400% |  |  | 0 | 1% to 4% | 1% | 4% | 0.4% | 1.6% | 0.6% | 2.4% | 1% to 10% | 347 | 138.8 | 208.2
Mid Rise OfficeHeating SystemDistrict heating and cooling systems | Mid Rise Office | Heating System | Central boilers serving dedicated outdoor air units and hot water radiators | 0.7 | District heating and cooling systems | 4.5 | -542.9% |  |  | $1 to $10 | 20% to 30% | 20% | 30% | 8% | 12% | 12% | 18% | 30%-75% | 347 | 138.8 | 208.2
Mid Rise OfficeHeating SystemAir source heat pumps | Mid Rise Office | Heating System | Central boilers serving dedicated outdoor air units and hot water radiators | 0.7 | Air source heat pumps | 3.5 | -400% |  |  | $1 to $10 | 20% to 30% | 20% | 30% | 8% | 12% | 12% | 18% | 30%-75% | 347 | 138.8 | 208.2
Mid Rise OfficeHeating SystemGround source heat pump | Mid Rise Office | Heating System | Central boilers serving dedicated outdoor air units and hot water radiators | 0.7 | Ground source heat pump | 4.5 | -542.9% |  |  | $1 to $10 | 20% to 30% | 20% | 30% | 8% | 12% | 12% | 18% | 30%-75% | 347 | 138.8 | 208.2
Educational FacilitiesDomestic Hot WaterHeat pump and electric resistance water heaters | Educational Facilities | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Heat pump and electric resistance water heaters | 3 | -400% |  |  | $1 to $10 | 1% to 5% | 1% | 5% | 0.4% | 2% | 0.6% | 3% | 1% to 15% | 347 | 138.8 | 208.2
Educational FacilitiesHeating SystemDistrict heating and cooling systems | Educational Facilities | Heating System | Central boilers | 0.675 | District heating and cooling systems | 4.5 | -566.7% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 30%-75% | 347 | 138.8 | 208.2
Educational FacilitiesHeating SystemAir source heat pumps | Educational Facilities | Heating System | Central boilers | 0.675 | Air source heat pumps | 3.5 | -418.5% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 30%-75% | 347 | 138.8 | 208.2
Educational FacilitiesHeating SystemGround source heat pump | Educational Facilities | Heating System | Central boilers | 0.675 | Ground source heat pump | 4.5 | -566.7% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 30%-75% | 347 | 138.8 | 208.2
Educational FacilitiesGas AppliancesElectric and induction ranges | Educational Facilities | Gas Appliances | Gas ranges | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $10 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 10% to 15% | 347 | 138.8 | 208.2
Big Box StoreDomestic Hot WaterElectric water heaters | Big Box Store | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Electric water heaters | 1 | -66.67% |  |  | 0 | 1% to 5% | 1% | 5% | 0.4% | 2% | 0.6% | 3% | 1% to 10% | 408 | 163.2 | 244.8
Big Box StoreHeating SystemRooftop air source heat pump with backup electric heat | Big Box Store | Heating System | Gas fired rooftop unit with direct expansion cooling coil | 1.75 | Rooftop air source heat pump with backup electric heat | 3.5 | -100% |  |  | $11 to $25 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 30% to 55% | 408 | 163.2 | 244.8
Low Rise OfficeDomestic Hot WaterHeat pump and electric resistance water heaters | Low Rise Office | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Heat pump and electric resistance water heaters | 3 | -400% |  |  | 0 | 1% to 5% | 1% | 5% | 0.4% | 2% | 0.6% | 3% | 1% to 10% | 333 | 133.2 | 199.8
Low Rise OfficeHeating SystemRooftop air source heat pump with electric baseboard | Low Rise Office | Heating System | Packaged rooftop unit with gas heating and direct expansion cooling and supplementary electric baseboard | 0.75 | Rooftop air source heat pump with electric baseboard | 3.5 | -366.7% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 30%-75% | 333 | 133.2 | 199.8
Strip MallDomestic Hot WaterElectric water heaters | Strip Mall | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Electric water heaters | 1 | -66.67% |  |  | 0 | 1% to 5% | 1% | 5% | 0.4% | 2% | 0.6% | 3% | 1% to 10% | 322 | 128.8 | 193.2
Strip MallHeating SystemRooftop air source heat pump with backup electric heat | Strip Mall | Heating System | Gas fired packaged rooftop unit with direct expansion cooling coil and supplementary electric heat | 0.75 | Rooftop air source heat pump with backup electric heat | 3.5 | -366.7% |  |  | $11 to $25 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 20% to 55% | 322 | 128.8 | 193.2
Mixed UseDomestic Hot WaterHeat pump and electric resistance water heaters | Mixed Use | Domestic Hot Water | Central domestic boiler | 0.7 | Heat pump and electric resistance water heaters | 3 | -328.6% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 322 | 128.8 | 193.2
Mixed UseHeating SystemDistrict heating and cooling systems | Mixed Use | Heating System | Central boilers | 0.675 | District heating and cooling systems | 4.5 | -566.7% |  |  | $1 to $10 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 20% to 40% | 322 | 128.8 | 193.2
Mixed UseHeating SystemAir source heat pumps | Mixed Use | Heating System | Central boilers | 0.675 | Air source heat pumps | 3.5 | -418.5% |  |  | $1 to $10 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 20% to 40% | 322 | 128.8 | 193.2
Mixed UseHeating SystemGround source heat pump | Mixed Use | Heating System | Central boilers | 0.675 | Ground source heat pump | 4.5 | -566.7% |  |  | $1 to $10 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 20% to 40% | 322 | 128.8 | 193.2
Mixed UseGas AppliancesElectric and induction ranges | Mixed Use | Gas Appliances | Gas ranges | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 25% | 322 | 128.8 | 193.2
Mixed UseGas AppliancesHeat pump electric dryers | Mixed Use | Gas Appliances | Gas clothes dryers | 0.45 | Heat pump electric dryers | 3.5 | -677.8% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 25% | 322 | 128.8 | 193.2
CondominiumDomestic Hot WaterHeat pump and electric resistance water heaters | Condominium | Domestic Hot Water | Central domestic boiler with auxillary storage tanks | 0.7 | Heat pump and electric resistance water heaters | 3 | -328.6% |  |  | $1 to $10 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 1% to 10% | 317 | 126.8 | 190.2
CondominiumHeating SystemDistrict heating/cooling systems | Condominium | Heating System | Central boiler serving fan coil units | 0.7 | District heating/cooling systems | 4.5 | -542.9% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 317 | 126.8 | 190.2
CondominiumHeating SystemAir source heat pumps | Condominium | Heating System | Central boiler serving fan coil units | 0.7 | Air source heat pumps | 3.5 | -400% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 317 | 126.8 | 190.2
CondominiumHeating SystemGround source heat pump | Condominium | Heating System | Central boiler serving fan coil units | 0.7 | Ground source heat pump | 4.5 | -542.9% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 317 | 126.8 | 190.2
CondominiumGas AppliancesElectric and induction ranges | Condominium | Gas Appliances | Gas ranges | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
CondominiumGas AppliancesHeat pump electric dryers | Condominium | Gas Appliances | Gas clothes dryers | 0.45 | Heat pump electric dryers | 3.5 | -677.8% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentDomestic Hot WaterHeat pump and electric resistance water heaters | Low Rise Rental Apartment | Domestic Hot Water | Central domestic boiler | 0.7 | Heat pump and electric resistance water heaters | 3 | -328.6% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentDomestic Hot WaterHeat pump and electric resistance water heaters | Low Rise Rental Apartment | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Heat pump and electric resistance water heaters | 3 | -400% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 21% to 30% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentHeating SystemDistrict heating and cooling systems | Low Rise Rental Apartment | Heating System | Central boiler and hydronic baseboard heating | 0.75 | District heating and cooling systems | 4.5 | -500% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 31% to 40% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentHeating SystemAir source heat pumps | Low Rise Rental Apartment | Heating System | Central boiler and hydronic baseboard heating | 0.75 | Air source heat pumps | 3.5 | -366.7% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 31% to 40% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentHeating SystemGround source heat pump | Low Rise Rental Apartment | Heating System | Central boiler and hydronic baseboard heating | 0.75 | Ground source heat pump | 4.5 | -500% |  |  | $11 to $25 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 31% to 40% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentGas AppliancesElectric and induction ranges | Low Rise Rental Apartment | Gas Appliances | Gas ranges | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Low Rise Rental ApartmentGas AppliancesHeat pump electric dryers | Low Rise Rental Apartment | Gas Appliances | Gas clothes dryers | 0.45 | Heat pump electric dryers | 3.5 | -677.8% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Single Family Home AttachedDomestic Hot WaterElectric water heaters | Single Family Home Attached | Domestic Hot Water | Water heaters (storage tank or tankless) | 0.6 | Electric water heaters | 1 | -66.67% |  |  | $1 to $10 | 11% to 20% | 11% | 20% | 4.4% | 8% | 6.6% | 12% | 11% to 20% | 317 | 126.8 | 190.2
Single Family Home AttachedHeating SystemAir source heat pumps | Single Family Home Attached | Heating System | Central furnace | 0.65 | Air source heat pumps | 3.5 | -438.5% |  |  | $1 to $10 | Up to 45% | 0 | 45% | 0% | 18% | 0% | 27% | Up to 45% | 317 | 126.8 | 190.2
Single Family Home AttachedGas Appliances Electric and induction ranges | Single Family Home Attached | Gas Appliances | Gas ranges | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Single Family Home AttachedGas Appliances Heat pump and electric dryers | Single Family Home Attached | Gas Appliances | Gas clothes dryers | 0.45 | Heat pump and electric dryers | 3.5 | -677.8% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Single Family Home DetachedDomestic Hot WaterElectric water heaters | Single Family Home Detached | Domestic Hot Water | Water heaters (storage tank) | 0.6 | Electric water heaters | 1 | -66.67% |  |  | $1 to $10 | 21% to 30% | 21% | 30% | 8.4% | 12% | 12.6% | 18% | 21% to 30% | 317 | 126.8 | 190.2
Single Family Home DetachedHeating SystemAir source heat pumps | Single Family Home Detached | Heating System | Central boilers | 0.675 | Air source heat pumps | 3.5 | -418.5% |  |  | $1 to $10 | Up to 55% | 0 | 55% | 0% | 22% | 0% | 33% | Up to 55% | 317 | 126.8 | 190.2
Single Family Home DetachedGas Appliances Electric and induction ranges | Single Family Home Detached | Gas Appliances | Gas ranges, cooktops, ovens | 0.55 | Electric and induction ranges | 0.85 | -54.55% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Single Family Home DetachedGas Appliances Heat pump and electric dryers | Single Family Home Detached | Gas Appliances | Gas clothes dryers | 0.45 | Heat pump and electric dryers | 3.5 | -677.8% |  |  | $1 to $5 | 1% to 10% | 1% | 10% | 0.4% | 4% | 0.6% | 6% | 5% to 20% | 317 | 126.8 | 190.2
Note on P2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming this is based on 40% (https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263)
Note on Q2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming this is based on 40% (https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263)
Note on R2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming this is based on 40% (https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263)
Note on S2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming this is based on 40% (https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263)
Note on U2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Energy split for natural gas and electricty is based on the to tal energy use breakdown provided in the following link https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263
Note on V2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Energy split for natural gas and electricty is based on the to tal energy use breakdown provided in the following link https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263
Note on W2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Energy split for natural gas and electricty is based on the to tal energy use breakdown provided in the following link https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-data-snapshots/energy-benchmarking-data-snapshots-for-all-building-types/24263

## References (hidden)
Electricity consumption intensity values (g CO2e/kWh electricity consumed) | CO2 emission factors for natural gas (g CO2/m3 natural gas) for 2025