## Instructions
Instructions to Use this Matrix
Step 1 — Net Zero Readiness Evaluation Matrix
Purpose:
This tab helps assess whether a building is ready to pursue a net-zero retrofit. It identifies strengths and gaps in data, systems, and planning.
Use this matrix early in your net-zero journey to determine whether the building is ready for a detailed electrification or decarbonization study.
How to Use:
1 | Review each category (e.g., Baselining, Control Systems, Load Reduction).
2 | Use the Readiness Rating (1–5) scale to score the building based on available evidence. The numbers currently shown are examples only, illustrating how the matrix works.
3 | The color scale automatically updates from red (low readiness) to green (high readiness) so you can easily identify which areas require improvement.
4 | Adjust the Weighting (%) column to reflect the importance of each category for your specific project. The example values provided are starting points — customize them to match your building’s priorities.
5 | Refer to the Matrix Scoring Guide at the top of the tab to interpret the readiness level (e.g., Developing, Advanced, Ready).
6 | Use the Notes / Actions column to capture key findings, recommendations, or follow-up steps. The example notes currently explain how the weighting was applied — feel free to remove or replace them with your own actions.
Step 2 - Identify Net Zero Pathways
Once you’ve determined that your building is ready to pursue net zero, the next step is to conduct a detailed energy study to evaluate potential pathways for achieving this goal. A net zero (or retrofit) pathway is a coordinated bundle of measures designed to achieve a specific emissions reduction target—such as net zero. Each pathway typically includes a combination of upgrades (e.g., heat pump + envelope + controls) that work together to meet your building’s performance and carbon reduction goals. The net zero pathway should include load reduction strategies, heat recovery opportunities (where applicable), and electrification measures. The low-carbon roadmap presented below outlines the range of opportunities that should be explored when developing potential pathways. However, not all measures will apply to every building—only those relevant to the specific site should be incorporated into the final pathway. Once several potential pathways have been identified through the energy study, proceed to Step 3 — Net Zero Pathway Evaluation Matrix to compare and evaluate each option.
Step 3 — Net Zero Pathway Evaluation Matrix
Purpose:
Once you’ve identified several potential net zero pathways through your detailed energy study, this tool can be used to compare and evaluate those options to determine the most effective path forward.
This tool supports transparent, data-driven decision-making during project prioritization or funding applications.
How to Use:
1 | Fill in the Weighting (%) column to reflect the relative importance of each evaluation criterion (e.g., Lifecycle Cost = 20%, Carbon Impact = 15%).
2 | Enter ratings (1–5) for each Net Zero Pathway column (F, G, H).
3 | Ratings automatically multiply by their weightings to generate a Weighted Score.
4 | Use the total weighted score at the bottom to compare pathways. The higher the score, the stronger the pathway alignment with your project goals.
5 | Add qualitative notes or explanations in the Notes / Actions column to provide context for each rating.
Tip:
Cells that are greyed out are locked, but if you wish to unlock them to make further edits you can use the password: NetZero
Step 4 — Implement Select Net Zero Pathway
Once the preferred net zero pathway has been selected, the next step is to develop and implement a phased plan for execution. In most cases, achieving net zero will require a multi-year implementation strategy, allowing upgrades to be staged over time to align with capital planning cycles, equipment replacement schedules, and available funding.

## Net Zero Readiness Matrix
Net Zero Readiness Evaluation Matrix Scoring Guide
Matrix Scoring Guide |  |  | Total Readiness Score Interpretation
Score | Readiness Level |  | Score Range | Readiness Level | Description
1 | Not Started |  | 5 | Ready | Ready to undertake detailed energy study to determine the retrofit opportunities and net zero pathways
2 | Early Awareness |  | 4 | Advanced | Most systems and data in place; only minor gaps remain.
3 | Developing |  | 3 | Developing | Some systems ready, but additional work is required before you are ready to begin your net zero pathway evaluation
4 | Advanced |  | 2 | Early Awareness | Limited data and systems; foundation work needed.
5 | Ready |  | 1 | Not Started | No data, systems, or plans in place.
Category | Assessment Criteria | Indicators / Evidence | Weighting (%) | Readiness Rating (1–5) | Notes / Actions
Baselining | • At least one full year of reliable energy data (electricity and fuel) is available through utility bills, submetering, or virtual metering platforms. • Data has been normalized for weather and occupancy to support comparison over time. | Utility bills, submetering data, EMIS | 10% | 5
Benchmarking | • The building has been benchmarked against comparable facilities using an accepted tool (e.g., ENERGY STAR, Portfolio Manager, or internal EUI comparison). • Benchmark results identify the building as a priority for decarbonization or retrofit action. | Benchmark report, ENERGY STAR score, internal EUI comparison, EMIS | 5% | 1 | It is not critical that you have benchmarked this building in order to pursue the net zero pathway - It could be identified as a high priority from other reasons such as end of life equipment, available funding, remaining electrical capacity etc.
Control System & Data | • A Building Automation System (BAS) is installed and capable of long-term trend logging (& remote access). • All major HVAC systems are connected, trended (or submeters are in place to monitor actual load) • Pneumatic control systems have been fully replaced with digital or DDC controls. | BAS trend data and screenshots | 10% | 4 | If you do not have a BAS you will likely want to set up metering (especially for DHW systems) to ensure you size your system appropriatetly. This can be done at the beginning of your net zero study.
Load Reduction | • Basic load reduction measures with proven financial returns have been implemented (e.g., high-efficiency sequences, VSDs, LED retrofits, optimized setpoints and schedules). | energy study reports, retrofit documentation, M&V Reports | 5% | 3 | It is not as imporant that you have done this already - you can do these as the first measures of your net zero retrofit pathway
Electrical Capacity | • Existing electrical service is known. • Either there is sufficient spare capacity to electrify or there is an appetite and budget to upgrade electrical service. | Electrical single-line diagram, electrical load analysis study, data directly from utility provider | 20% | 5
Equipment Near End of Life | • Major mechanical systems (e.g., boilers, chillers, RTUs, DHW systems) are approaching or beyond their expected service life (typically within 5 years). | Equipment inventory, maintenance logs, condition assessment reports | 30% | 4
Funding | • The organization has access to or eligibility for incentives, rebates, or grants to support electrification and retrofit projects. • OR there is capacity to manage the capital premium associated with net-zero or low-carbon investments (via internal capital planning or external financing). | Funding applications, internal capital plans, grant approvals | 20% | 3
|  | Total | 100% | 25
|  |  | Weighted Score (0-5) | 3.9

## Net Zero Pathway Evaluation
Net Zero Pathway Evaluation Matrix Scoring Guide
Category | Metric | Category Notes | How to Rate (1–5) | Weighting (%) | Net Zero Pathway #1 | Net Zero Pathway #2 | Net Zero Pathway #3 | Notes/Actions
Lifecycle Cost | Net Present Value - NPV ($) | Total cost of ownership over project life. Including all incentives and considering the incremental cost of replacing end of life equipment. | 1 – Lowest NPV 5 – Highest NPV (Include negative NPV values, as most cost effective pathway may still have a negative NPV compared to business as usual) | 15% | 4 | 3 | 2
Carbon Impact | Lifetime GHG savings (tonnes) | How many tonnes of GHGs does the pathway save over the lifetime? | 1 – <20% reduction (does not meet targets) 3 – 40–60% reduction (meets targets) 5 – ≥90% reduction (exceeds targets) | 10% | 3 | 4 | 5
Energy Impact | Site EUI Reduction (%) | How much total site energy use is reduced through this retrofit? (compared to baseline consumption) **The best net zero pathways will combine demand reduction and fuel switching to reduce overall site energy consumption rather than increase it | 1 – <5% reduction 3 – 15–30% reduction 5 – ≥50% reduction | 15% | 3 | 2 | 3
Comfort, Safety & Resilience | IAQ, temperature control and occupant well-being | Will this retrofit improve building resilience or occupant comfort and safety? (e.g. HRVs, CO2 monitoring, additional ventilation, cooling, battery storage for power outages) | 1 – No improvement or negative impact 3 – Noticeable improvement 5 – Major enhancement to comfort, safety and/or resilience | 20% | 2 | 1 | 1
Disruption | Occupant impact | How disruptive will this improvement be to occupants? For MURBs, will residents have to move out temporarily? | 1 – Major disruption (vacate required) 3 – Moderate disruption 5 – Minimal disruption | 10% | 4 | 3 | 1
Risk and Feasibility | Technical and financial certainty | Are there significant risks/unknowns that could increase costs (e.g. hazmat, high level of study, old building, limited drawings, uncertainty with condition of piping, structural or mechanical unknowns, new untested equipment) | 1 – High uncertainty or risk 3 – Manageable risk 5 – Proven, low-risk pathway | 20% | 2 | 2 | 4
Stakeholder Support | Owner/tenant/community alignment | Level of owner/tenant/community support; alignment with policy/ESG commitments. Are there multiple owners or different tenant groups with different priorities? | 1 – Opposition or no engagement 3 – Moderate support or policy alignment 5 – Full endorsement, strong ESG alignment | 10% | 4 | 3 | 5
Add others here
Add others here
Totals |  |  |  | 100% | 2.95 | 2.35 | 2.85